## EPICS
EPICS Names | Description | Units
QW_T_miA | Temp A at manifold inlet | K | Cernox | Additional signals to consider:
QW_T_moA | Temp A at manifold outlet | K | Cernox
QW_T_hxiA | Temp A at heat exchanger inlet | K | Cernox | Phytron brake
QW_T_hxoA | Temp A at heat exchanger outlet | K | Cernox | Phytron home switch
QW_T_piA | Temp A at pump inlet | K | Cernox | GV open switch
GV closed switch
QW_T_miB | Temp B at manifold inlet | K | Cernox | Turbo status *5?
QW_T_moB | Temp B at manifold outlet | K | Cernox | CCG *5?
QW_T_hxiB | Temp B at heat exchanger inlet | K | Cernox | Ballast vacuum
QW_T_hxoB | Temp B at heat exchanger outlet | K | Cernox
QW_T_piB | Temp B at pump inlet | K | Cernox
QW_T_ladderA | Temp A on dummy tgt ladder | K
QW_T_USdmA | Temp A on upstream dummy frame | K
QW_T_DSdmA | Temp A on downstream dummy frame | K
QW_T_phytronA | Temp A on Phytron motor | K
QW_T_tableA | Temp A on Horizontal Motion table | K
QW_T_ladderB | Temp B on dummy tgt ladder | K
QW_T_USdmB | Temp B on upstream dummy frame | K
QW_T_DSdmB | Temp B on downstream dummy frame | K
QW_T_phytronB | Temp B on Phytron motor | K
QW_T_tableB | Temp B on Horizontal Motion table | K
QW_T_solidA | Temp A on solid target frame | K
QW_T_solidB | Temp B on solid target frame | K
QW_T_spareA |  | K
QW_T_spareB |  | K
QW_T_pumpA | Temp A on pump motor house | K
QW_T_pumpB | Temp B on pump motor house | K
K
QW_T_4kjt | Coolant Temp at outlet of 4K JT valve | K | Cernox
QW_T_4ko | Temp of returning 4K coolant | K | Cernox
QW_T_15kjt | Coolant Temp at outlet of 15K JT valve | K | Cernox
QW_T_15ko | Temp of returning 15K coolant | K | Cernox
QW_Pmp_TachSet | Set value for pump tach | Hz
QW_Pmp_VSet | Set value for pump voltage | Volts
QW_Pmp_I1Set | Set value for pump current phase 1 | Amps
QW_Pmp_I2Set | Set value for pump current phase 2 | Amps
QW_Pmp_I3Set | Set value for pump current phase 3 | Amps
QW_Pmp_TachRead | Read value for pump tach | Hz
QW_Pmp_VRead | Read value for pump voltage | Volts
QW_Pmp_I1Read | Read value for pump current phase 1 | Amps
QW_Pmp_I2Read | Read value for pump current phase 2 | Amps
QW_Pmp_I3Read | Read value for pump current phase 3 | Amps
QW_Pmp_Status1 | Pump controller status bits
QW_Pmp_Status2 | Pump controller status bits
QW_HPH_ISet | High Power Heater set current limit | Amps
QW_HPH_VSet | High Power Heater set voltage | Volts
QW_HPH_PSet | High Power Heater set (calculated) power | Watts
QW_HPH_IRead | High Power Heater read current | Amps
QW_HPH_VRead | High Power Heater read voltage | Volts
QW_HPH_PRead | High Power Heater read power | Watts
QW_HPH__PID | Pid mode on or off
QW_HPH_TSet | HPH set temperature | K
QW_HPH_TRead | HPH read/current temperature | K
QW_HPH_Beam_Comp_Switch | HPH beam compensation switch
QW_pbeam | Calculated beam power | Watts
QW_ibeam | Beam current | uA
QW_HPH_Pmax | Maximum Heater Power | W
QW_HPH_Pman | Manual power setting | W
QW_HPH_R | Heater resistance | Ohms
QW_HPH_OnOff | Heater mode
QW_HPH_bmcomp1 | beam compensation parameter 1 (length) | cm
QW_HPH_bmcomp2 | beam compensation parameter 2 (density) | g/cc
QW_HPH_bmcomp3 | beam compensation parameter 3 (dE/dx) | MeV/g/cm^2
QW_HPH_bmcomp4 | beam compensation parameter 4 (spare)
QW_HPH_Prop | PID proportinal gain (typ 600)
QW_HPH_Integ | PID integral gain (typ 40)
QW_HPH_Deriv | PID derivative gain (typ 0)
QW_HPH_Scan | Scan time for PID (typ 1) | s
QW_HPH_dmin | minimum change in power per scan | W
QW_HPH_dmax | maximum change in power per scan | W
QW_JT_4Kset
QW_JT_4KRead
QW_JT_4KStep | 4K JT Step size
QW_JT_15KSet
QW_JT_15LRead
QW_JT_15KStep | 15K JT Step size
QW_Phy_ENCSet | Hor. Motion Phytron set stepper position
QW_Phy_VSet | Hor. Motion Phytron set Voltage | Volts
QW_Phy_ISet | Hor. Motion Phytron set current | Amps
QW_Phy_BrakeSet | Hor. Motion Phytron set brake value
QW_Phy_ENCRead | Hor. Motion Phytron read stepper position
QW_Phy_VRead | Hor. Motion Phytron read Voltage | Volts
QW_Phy_IRead | Hor. Motion Phytron read current | Amps
QW_Phy_BrakeRead | Hor. Motion Phytron read brake value
QW_Phy_Prog | Hor. Motion Phytron program number
QW_Phy_Out1 | Hor. Motion Phytron output word 1
QW_Phy_Out2 | Hor. Motion Phytron output word 2
QW_Phy_In1 | Hor. Motion Phytron input word 1
QW_Phy_In2 | Hor. Motion Phytron input word 2
QW_Phy_Switches | Hor. Motion Phytron limit switch readback
QW_Phy_ResPos | Hor. Motion resistive position readout
QW_EC5_ENCSet | Lifter EC5 set stepper position
QW_EC5_VSet | Lifter EC5 set Voltage | Volts
QW_EC5_ISet | Lifter EC5 set current | Amps
QW_EC5_BrakeSet | Lifter EC5 set brake value
QW_EC5_ENCRead | Lifter EC5 read stepper position
QW_EC5_VRead | Lifter EC5 read Voltage | Volts
QW_EC5_IRead | Lifter EC5 read current | Amps
QW_EC5_BrakeRead | Lifter EC5 read brake value
QW_EC5_Prog | Lifter EC5 program number
QW_EC5_Out1 | Lifter EC5 output word 1
QW_EC5_Out2 | Lifter EC5 output word 2
QW_EC5_In1 | Lifter EC5 input word 1
QW_EC5_In2 | Lifter EC5 input word 2
QW_EC5_Switches | Lifter EC5 limit switch readback
QW_EC5_AxisStatus
QW_EC5_DriveStatus
QW_EC5_SystemStatus
QW_EC5_ResPos | Lifter EC5 resistive position readout
QW_PT4 | Gas panel pressure transducer PT4 | psia
QW_PT9 | Gas panel pressure transducer PT9 | psia
QW_PT7 | Gas panel pressure transducer PT7 | psia
QW_PT87 | Gas panel pressure transducer PT87 | psia
QW_PT77 | Gas panel pressure transducer PT77 | psia
QW_PT_Scatt_Chamber | Scattering Chamber Vacuum | psia
QW_PT_Scatt_Chamber_switch | Scattering Chamber vacuum switch | psia
HC_ValveBox_Pos | Warm return valve position | % open
HC_ValveBox_Temp | Warm return temp | K
QW_TgtX0 | X (Hor) stepper pos for Tgt 0
QW_TgtY0 | Y (Ver) stepper pos for Tgt 0
QW_TgtX1
QW_TgtY1
QW_TgtX2
QW_TgtY2
QW_TgtX3
QW_TgtY3
QW_TgtX4
QW_TgtY4
QW_TgtX5
QW_TgtY5
QW_TgtX6
QW_TgtY6
QW_TgtX7
QW_TgtY7
QW_TgtX8
QW_TgtY8
QW_TgtX9
QW_TgtY9
QW_TgtX10
QW_TgtY10
QW_TgtX11
QW_TgtY11
QW_TgtX12
QW_TgtY12
QW_TgtX13
QW_TgtY13
QW_TgtX14
QW_TgtY14
QW_TgtX15
QW_TgtY15
QW_TgtX16
QW_TgtY16
QW_TgtX17
QW_TgtY17
QW_TgtX18
QW_TgtY18
QW_TgtX19
QW_TgtY19
QW_TgtX20
QW_TgtY20
QW_TgtX21
QW_TgtY21
QW_TgtX22
QW_TgtY22
QW_TgtX23
QW_TgtY23
QW_TgtX24
QW_TgtY24
QW_TgtX25
QW_TgtY25
QW_TgtX26
QW_TgtY26
QW_Tgt_Raster0 | Raster requirement for Tgt 0
QW_Tgt_CurLim0 | Beam Current Limit for Tgt 0
QW_Tgt_Raster1
QW_Tgt_CurLim1
QW_Tgt_Raster2
QW_Tgt_CurLim2
QW_Tgt_Raster3
QW_Tgt_CurLim3
QW_Tgt_Raster4
QW_Tgt_CurLim4
QW_Tgt_Raster5
QW_Tgt_CurLim5
QW_Tgt_Raster6
QW_Tgt_CurLim6
QW_Tgt_Raster7
QW_Tgt_CurLim7
QW_Tgt_Raster8
QW_Tgt_CurLim8
QW_Tgt_Raster9
QW_Tgt_CurLim9
QW_Tgt_Raster10
QW_Tgt_CurLim10
QW_Tgt_Raster11
QW_Tgt_CurLim11
QW_Tgt_Raster12
QW_Tgt_CurLim12
QW_Tgt_Raster13
QW_Tgt_CurLim13
QW_Tgt_Raster14
QW_Tgt_CurLim14
QW_Tgt_Raster15
QW_Tgt_CurLim15
QW_Tgt_Raster16
QW_Tgt_CurLim16
QW_Tgt_Raster17
QW_Tgt_CurLim17
QW_Tgt_Raster18
QW_Tgt_CurLim18
QW_Tgt_Raster19
QW_Tgt_CurLim19
QW_Tgt_Raster20
QW_Tgt_CurLim20
QW_Tgt_Raster21
QW_Tgt_CurLim21
QW_Tgt_Raster22
QW_Tgt_CurLim22
QW_Tgt_Raster23
QW_Tgt_CurLim23
QW_Tgt_Raster24
QW_Tgt_CurLim24
QW_Tgt_Raster25
QW_Tgt_CurLim25
QW_Tgt_Raster26
QW_Tgt_CurLim26
QW_ResEncX | ADC value of horizontal resistive encoder
QW_ResEncY | ADC value of vertical resistive encoder
QW_ResEnc_TgtX0 | Resistive Encoder X (Hor) for Tgt 0
QW_ResEnc_TgtY0 | Resistive Encoder Y (Ver) for Tgt 0
QW_ResEnc_TgtX1
QW_ResEnc_TgtY1
QW_ResEnc_TgtX2
QW_ResEnc_TgtY2
QW_ResEnc_TgtX3
QW_ResEnc_TgtY3
QW_ResEnc_TgtX4
QW_ResEnc_TgtY4
QW_ResEnc_TgtX5
QW_ResEnc_TgtY5
QW_ResEnc_TgtX6
QW_ResEnc_TgtY6
QW_ResEnc_TgtX7
QW_ResEnc_TgtY7
QW_ResEnc_TgtX8
QW_ResEnc_TgtY8
QW_ResEnc_TgtX9
QW_ResEnc_TgtY9
QW_ResEnc_TgtX10
QW_ResEnc_TgtY10
QW_ResEnc_TgtX11
QW_ResEnc_TgtY11
QW_ResEnc_TgtX12
QW_ResEnc_TgtY12
QW_ResEnc_TgtX13
QW_ResEnc_TgtY13
QW_ResEnc_TgtX14
QW_ResEnc_TgtY14
QW_ResEnc_TgtX15
QW_ResEnc_TgtY15
QW_ResEnc_TgtX16
QW_ResEnc_TgtY16
QW_ResEnc_TgtX17
QW_ResEnc_TgtY17
QW_ResEnc_TgtX18
QW_ResEnc_TgtY18
QW_ResEnc_TgtX19
QW_ResEnc_TgtY19
QW_ResEnc_TgtX20
QW_ResEnc_TgtY20
QW_ResEnc_TgtX21
QW_ResEnc_TgtY21
QW_ResEnc_TgtX22
QW_ResEnc_TgtY22
QW_ResEnc_TgtX23
QW_ResEnc_TgtY23
QW_ResEnc_TgtX24
QW_ResEnc_TgtY24
QW_ResEnc_TgtX25
QW_ResEnc_TgtY25
QW_ResEnc_TgtX26
QW_ResEnc_TgtY26
CFI6731C | 15k Flow | g/s
CTD673 | 15K Supply temp at ESR | K
CPI673 | 15K Supply pressure at ESR | atm
CTD9541 | 20K return temp at ESR | K
CPI9541 | 20K return pressure at ESR | atm
haCryo_15K_Total_F | sum of Hall A and Hall C 15K flows | g/s
CFI60DLP | "dirty flowrate" at ESR (warm return) | g/s
CTD6614 | Hall A 15K supply temp | K
CFI6711C | 4k Flow | g/s
CTD671SC | 4K Supply temp at ESR | K
CPI671SC | 4K Supply pressure at ESR | atm
CTD672 | 5K return temp at ESR | K
CPI672 | 5K return pressure at ESR | atm
QWBCM1 | Beam current in Hall C | uA
QWBCM2 | Beam current in Hall C | uA
QWBCM3 | Beam current in Hall C | uA
QWBCM4 | Beam current in Hall C | uA
QWGV_Status | Status bits of the gate valves
QWHPHIset | Max Heater Current Set
QWHPHIDACset | Max Current DAC Set
QWHPHVDACset | Voltage DAC Set
QWHPHManual | Manual power setting
QWHPHAuto | auto power setting
QWHPHheat_pid.ORBV | Cur Pos
QWHPHheat_pid.OVAL | Cur Out
QWHPHheat_pid.CVAL | Cur Inp
QWHPHheat.pidS | Output
QWHPHheat_pid_VAL | Set Value
QWHPHmode_bypass.VAL | Heater mode
QWheat_tot | Total Power
QWbeam_heat | Beam Power