## HDSSM's PLC I-0 Table
Dipole's PLC I/O Usage Table
Module | IF16 | IF16 | IF16 | IF16 | IF16 | IF16 | IF16 | IF16
Configuration | Single_Ended voltage | Single_Ended voltage | Single_Ended voltage | Single_Ended voltage | Single_Ended voltage | Single_Ended voltage | Single_Ended voltage | Single_Ended voltage
Chasis Slot # | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Channel
0 | T_He_LCLW | T_LN2_C2_1 | T_LN2_C4_1
1 | T_He_RCLW | T_LN2_C2_2 | T_LN2_C4_2
2 | T_LN2_C1_1 | T_LN2_C2_3 | T_LN2_C4_3
3 | T_LN2_C1_2 | T_LN2_C2_4 | T_LN2_C4_4
4 | T_LN2_C1_3 | T_LN2_C2_5 | T_LN2_C4_5
5 | T_LN2_C1_4 | T_LN2_C2_6 | T_LN2_C4_6
6 | T_LN2_C1_5 | T_LN2_C2_7 | T_LN2_C4_7
7 | T_LN2_C1_6 | T_LN2_C2_8 | T_LN2_C4_8
8 | T_LN2_C1_7 | T_LN2_C3_1
9 | T_LN2_C1_8 | T_LN2_C3_2
10 | T_LN2_supp | T_LN2_C3_3
11 | T_HX1_N2 | T_LN2_C3_4
12 | T_HX2_N2 | T_LN2_C3_5
13 | T_LN2_tank | T_LN2_C3_6
14 |  | T_LN2_C3_7
15 |  | T_LN2_C3_8
Note on C9: pappala: PRT

## Signal list
I/O Device
Signal description | Range | Number of wires | Qty | Redundant Qty | Description
Cryogenics
Temperature
Temperature Sensor | 40K to 300K | 4 | 2 |  | PT102: 100Ohm Platinum Resistance sensor
Temperature Sensor | 40K to 300K | 4 | 4 |  | PT102 New:To be installed-100Ohm Platinum resistance sensor:
Temperature Sensor( Coils) | 4K to 300K | 4 | 32 | 32 | PT-100 Platinum Resistance Thermometers existing inside coils
Temperature Sensor( Coils) | 4K to 300K | 4 | 29 |  | Allen-Bradley 1/8 watt Carbon Resistance Thermometers
Temperature Sensor | <60K | 4 | 7 |  | Thin Film Carbon Glass 4-wire
Thermocouples |  |  | 44 |  | Copper-Constantan
|  | Total | 118
Gas Flow Controllers
+ Lead He Gas Flow |  | 5 | 1 |  | MKS 1749A-02000SV +24Vdc input 4-20mA output
- Lead He Gas Flow |  | 5 | 1 |  | MKS 1749A-02000SV +24Vdc input 4-20mA output
Vacuum
LH Thermovac TR206 |  | 2 | 1 |  | Leybold Combivac CM 31
LH PenningVac PR 35 |  | 2 | 1 |  | Leybold Combivac CM 31
Controller | 120 Vac cord | 3 | 1
Pressure
LN2 Pressure |  | 6 | 1
LHe Pressure(tank) |  | 6 | 1
He supply |  | 6 | 1
He return |  | 6 | 1
Liquid Level
LN2 Level | 0 - 100 % |  | 1
Relay Contact 1 |  |  | 1 |  | setpoint 1
Relay Contact 2 |  |  | 1 |  | setpoint 2
Power Cycle relay |  |  | 1 |  | DC relay to power cycle 120Vac power
LHe Level | 0 - 100 % |  | 1 |  | Constant current source
Relay Contact 1 |  |  | 1 |  | setpoint 1
Relay Contact 2 |  |  | 1 |  | setpoint 2
Power Cycle relay |  |  | 1 |  | DC relay to power cycle 120Vac power
Valves
JT Valves |  | 4 | 11 |  | Globe Motor (24 VDC @ 0.8A)
JT LVDT |  | 5 | 11 |  | Macro sensors
Electric Valve Motor | -6-100% | 4 | 3 |  | Globe Motor (24 VDC @ 0.8A)
Electric valve Position |  | 6 | 3 |  | Macro Sensors LVC-2402
Voltage Readings
Main Coil Voltages |  |  | 24 |  | 8 are to be wired to the Quench detector
Main Coil Transistion Leads |  |  | 4
Strain Gauges
Gauge |  | 4 | 24 |  | Omega Constantan SG-7/340-XY47
Power Supply
PSU interlocks and status signals |  |  | 5 |  | Interlock and status signals from PSU
PSU interlocks |  |  | 2 |  | Interlock signals to the PSU from PLC
PSU reset signal |  |  | 1 |  | Rest signal to PSU and diodes
PSU coarse current signal |  |  | 1 |  | 3 V dc +/- dac output from PSU
Interlock Signals
Fast Discharge |  |  | 2
Slow Discharge |  |  | 2
Quench Detector
Danfysik 4 channel |  | P5 | 11 |  | Interlock signals
|  | P5 | 3 |  | Relay contact
|  | P6 | 2 |  | Reset signal
|  | P7 | 2 |  | Power
Note on F30: pappala: Ref. Quads (Use american) Check American magnetics.Ask suggestion
Note on D46: pappala: Changed
Note on D40: pappala: Changed
Note on F24: pappala: Suggestion
Note on F8: pappala: Platinum Resistance Thermometers are the PT100's.Curves given in documentation.

## Coil 1
Coil 1
Signal description | Location | No. | Redundant | No. of wires | Wire colors | Cable number | Cable color
Strapped in 2's
P1
PT 100 |  | 8 | 8 | 4 | Purple | Belden M 9539 | Orange[1] | P1
(new) | LN2 supply |  |  |  | Blue |  | Purple | P2
Yellow
[5 empty] | Green |  | Blue [2] | P1
[5 empty] | P2 |  | Green | P2
Black
| LN2 return |  |  |  | Orange |  | White[3] | P2
[5 empty] | Red |  | Yellow | P1
Brown
[7 empty] | Red[4] | P2
[7 empty] | Brown | P1
Strain gauges |  | 6 |  | 4 | Blue | Belden M 9539 | Blue+White
[5 empty] | Red |  | Red+Green
[5 empty] | Green |  | Red+White
[5 empty] | White |  | Orange+Red
Orange+Grey
Red+Blue
Voltage Taps |  | 6 |  | 1 | Marked S25-S30 |  | White cable
Thermocouples | 24-No. Outer inlet of coil#1N2 shields | 9 |  | 2 | 24-27-> Blue+Red |  | White cable
| 25-So.Outer inlet of Coil#1 N2 shields |  |  |  | 28-32->Brown sheath
26-No. Inner inlet of Coil#1 N2 shields
27-So. Inner inlet of Coil#1 N2 shields
28-No. Middle outer of Coil#1 N2 shields
29-So. Middle outer of Coil#1 N2 shields
30-No. Inner outer of Coil#1 N2 shields
31-No. Outer outlet of Coil#1 N2 shields
32-So. Outer outlet of Coil#1 N2 shields
No.->North
So->South
| 70 & 71 | 2 |  | 2 | pink
brown
Carbon Resistance Thermometers | 72-No location | 8 |  | 3 | White
| 73-Bottom of Coil section A& B |  |  |  | Black
| 74-Bottom of Coil #1(IG) on straps |  |  |  | Green
75-Bottom of coil section C of Coil #1
76-No location
77- Bottom of coil Section C of Coil#1
78-No location
79-No location
Silicon Diodes | 12,13,14,15,19,20,21 | 12 |  | 3 | Brown
Green
White+Brown
| 16,17,18,22 |  |  | 2 | Brown
White+Brown
| 23 |  |  | 2 | Black
White+Black
Note on C51: pappala: Taped to the CRT bunch
Note on G35: pappala: Acc. to old docu. 25 corresponds to 84 26-81;27-85;28-82;29-83;30-80
Note on C46: pappala: Label missing on wire
Note on J9: pappala: Ref: Wire colors
Note on J10: pappala: Ref. Wire colors
Note on B66: pappala: Update information

## Summary
|  |  |  | PT-100 | CRT | Carbon glass | Thermocouples | Voltage taps | Strain gauges | Flow indicators | Vacuum gauges | Pressure gauges | Liquid level | Valves
|  | Coil 1 |  | 8+8R | 8 | 0 | 11 | 6 | 6 | 0 | 0 | 0 | 0 | 0
|  | Coil 2 |  | 8+8R | 7 | 0 | 11 | 5 | 6 | 0 | 0 | 0 | 0 | 0
|  | Coil 3 |  | 8+8R | 7 | 0 | 11 | 5 | 6 | 0 | 0 | 0 | 0 | 0
|  | Coil 4 |  | 8+8R | 7 | 0 | 11 | 4 | 6 | 0 | 0 | 0 | 0 | 0
|  | LHe tank |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1
|  | He supply |  | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3
|  | He return |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1
|  | Warm He from magnet |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
|  | LN2 tank |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1
|  | LN2 supply |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
|  | Nitrogen jacket |  | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
|  | Vacuum jacket |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0
Controller | 120 Vac cord | 3 | 1
|  | Current leads |  | 2 | 0 | 2 | 0 | 4 | 0 | 2 | 0 | 0 | 0 | 2
|  | Heat exchangers |  | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
5
|  | Total |  | 43 | 29 | 7 | 44 | 29 | 24 | 2 | 2 | 4 | 2 | 16
32R
Note on I23: pappala: Coil to coil splice voltage taps.