## Sheet1
Heat Exchanger Calculations
Units
Inside Heat Trasfer Coefficient
Assuming Gas Temp as 195 K
µ(viscosity) |  | 1.5e-05
Prandtl Number |  | 0.667
Specific Heat(KJ/KgK) |  | 5194
Area of flow inside the tube (1/2" O.D,0.049 thk) Ai |  |  |  | Ai | 8.1762e-05 | m2
Inside Dia |  |  |  | Di | 0.010203 | meters
Mass Flow Rate per Unit Area |  |  |  | Gi | 122.3068 | kg/m2s
Reynolds Number (Di*Gi/µ) |  |  |  | Re | 83193.4296
|  |  |  | Dm | 0.13642 | meters
|  |  |  | Bc | 1.4184
Colburn J-Factor |  |  |  | Jh | 0.0033847
|  |  |  | hi | 2816.5607 | W/m2K
Outer Diameter Of tube |  |  |  | Do | 0.01269 | meters
Outside Heat Trasfer Coefficient
|  |  | thickness of fin |  | 0.02 |  | 0.035
Assuming Gas Temp as 190 K
µ(viscosity) |  | 1.48e-05
Prandtl Number |  | 0.667
Specific Heat(KJ/KgK) |  | 5193
Area occupied by one fin |  |  |  | Afin | 6.4418e-06 | m2 | 1.1273e-05
Area Occupied by 690 fins(One turn occupies 690 fins) |  |  |  | A,690 fins | 0.0044448 |  | 0.0077785
Mass Flow Area for 80 K Gas |  |  |  | Ao | 0.0066858 |  | 0.0033522
Area of flow outside the tube |  |  |  | Ao | 0.0066858 | m2 | 0.0033522
Mean Dia |  |  |  | Dm | 0.13959 | meters | 0.13959
Mass Flow Rate per Unit Area |  |  |  | Gi | 1.4957 | kg/m2s | 2.9832
Reynolds Number (Di*Gi/µ) |  |  |  | Re | 14107.5547 |  | 28137.1413
Colburn J-Factor |  |  |  | Jh | 0.0050173 |  | 0.0038542
Convective Heat Transfer Coefiicient |  |  |  | ho | 51.0483 | W/m2K | 78.2124
Thermal Conductivity Of Copper |  |  |  | Kw | 400 | W/mK | 400
Overall Heat Trasfer Coefficient
Overall Heat Transfer Coefficient |  |  |  | Uo | 49.9143 | W/m2K | 75.5814
Total Surface Area of 1/2in tube |  |  |  | Atube | 0.97908 |  | 0.97908
Total Surface Area of 19351 fins |  |  |  | Afins | 0.00079938 |  | 0.00079938
Over All Heat transfer Area(Atube+Afins) |  |  |  | Aoverall | 16.4479 | m2 | 16.4479
|  |  |  | UoAo | 820.9866 | W/k | 1243.1578
|  |  |  | Cmin | 51.93 | W/K | 51.93
NTU*Cmin=UoAoverall |  |  |  | NTU | 15.8095 |  | 23.9391
Surface Temperatures
Th,ave | 192.5
Tc,ave | 187.4375
Average temperature of Hot Wall |  |  |  | Thw | 192.3884 | K
Average temperature of Cold Wall |  |  |  | Tcw | 192.3875 | K
Used Temperatures
The mean hot film Temperature |  |  |  | Thm | 192.4442 | 195
The mean cold film Temperature |  |  |  | Tcm | 189.9125 | 190
Number Of Tube Passages |  |  |  | N | 28 |  | 28
NTU per pass |  |  |  | Np | 0.56462 |  | 0.85497
Cr |  |  |  | Cr | 0.99942 |  | 0.99942
Effectiveness of Counter Flow Heat Exchanger
ξ=(1-exp(-NTU(1-Cr))/(1-Cr*exp(-NTU(1-Cr)) |  |  |  | ξ | 0.94076 |  | 0.96017 | 0
Temperature of Cold return ξ=(Tc2-Tc1)/Th1-Tc1) |  |  |  | Tc2 | 286.9683 |  | 291.2369
|  |  |  | Tc1 | 80 |  | 80
|  |  |  | Th1 | 300 |  | 300
Q=mcpdth=mcpdtc |  |  |  | Th2 | 93 |  | 93
|  |  |  | Tcavg | 183.4841 |  | 185.6185
|  |  |  | Thavg | 196.5 |  | 196.5
|  |  |  | Dtavg | 13.0159 |  | 10.8815
Pass Effectiveness(1-ξp)=exp{-(1/Cr)[1-exp(-NTUCr/Np)]} |  |  |  | (1-ξp) | 0.36767 |  | 0.36767
|  |  |  | ξp | 0.63233 |  | 0.63233
Calculating the Heat Loss Through Fins | [6 empty] | t=.035
Temperature difference of two gases |  |  |  | ΔT | 220 |  | 220
Outer Radius |  |  |  | re | 0.01269 | m | 0.01269
Inner radius |  |  |  | ro | 0.0063452 | m | 0.0063452
Thickness of the Fin |  |  |  | t | 0.00050761 | m | 0.00088832
Thermal conductivity Of Copper |  |  |  | K | 400 | W/mK | 400
Heat Transfer Coefficient |  |  |  | ho | 51.0483 | W/m2K | 78.2124
m=sqrt(2*ho/K*t) |  |  |  | m | 22.4238 |  | 20.9815
|  |  |  | mre | 0.28457 |  | 0.26626
|  |  |  | mro | 0.14228 |  | 0.13313
Heat Dissipation from One fin |  |  |  | Qo | 0.49162 | W | 0.47343
Total of 19351 fins |  |  |  | Qfins | 9513.2806 | W | 9161.3449
Heat Dissipation from Copper Tube |  |  |  | Qcu,tube | 650.4851 | W | 833.1986
Total Heat from fins and Copper tube |  |  |  | Qtotal | 10163.7657 | W | 9994.5434
Heat calculated from mcpdt is |  |  |  | Q | 11400 | W | 11400
Heat Dissipation from One fin |  |  |  | Qo | 0.095631 | 730.8986 | 0.15659
|  |  |  | Qtot | 1850.5621 |  | 3030.1883
|  |  |  | DT | 15.5972 |  | #DIV/0!