## Slide 1: Hall B Gas System Controls
Physics Detector Support Group

## Slide 2: Hall B Controls Setup
Custom controls interface chassis with touchscreen monitor
National Instruments compact RIO DaQ and controls.
National Instruments LabView software in gas shed.
Hall B’s gas systems are controlled by three individual setups which work in concert over the slow controls network (160) to provide operational control to a user in the Hall B gas shed, while also providing monitoring data in the form of process variables to the CLAS 12 EPICs system in the counting house.
Process Variable to EPICS
EPICS monitoring screen in counting house.

## Slide 3: Hall B DC Gas Controls GUI

## Slide 4: Hall B DC Gas EPICS Monitoring Screen

## Slide 5: Gas System Controls
4 Detector gas system controls have been developed and are being tested.
  Drift Chamber
  Low Threshold Cherenkov Counter
  High Threshold Cherenkov Counter
  Silicon Vertex Tracker
3 Detector systems in planning/development
(No purchased equipment)
  RICH
  Micro-Megas Vertex Tracker
  Forward Tagger

## Slide 6: Hall B Gas Controls Connections
LabView Code
LabView Code
Gas Flow Control and Monitoring
MFC power
Sensor power
Sensor signal
Sensor signal
PC with LabView Software
NI 9035 cRIO
Gas Controls Interface chassis
System sensor
MKS GE50/250
Mass Flow Controller
Network switch
Gas Flow Monitoring
GUI Controls

## Slide 7: Controls system locations
Hall B End station

## Slide 8: Hall B DC Gas Controls
Network
hb-crio-gs
Network
Switch
MKS GE250 Mass Flow Controller (x3)
Gas Control
Network
Oxy_IQ O2 sensor (x3)
Easidew Moisture sensor (x3)
Analog Input
MKS 579 Mass Flow Transducers (x2)
Gas Monitoring
Panametrics S3 TCU(x2)
MKS 122 Absolute Pressure Transducer (x2)
hb-crio-sf
Network
Switch
Network
Pressure Control Valve sets (x2)
Analog Input
Pressure Control
Analog Output
MKS 223 Differential Pressure Transducer (x2)
MKS GE250 Mass Flow Controller (x4)
Ar/CO2 Gas Mixing Control
Gas Shed
Space Frame

## Slide 9: Hall B LTCC Gas Controls
Network
hb-crio-gs
Network
Switch
MKS GE250 Mass Flow Controller (x1)
Gas Flow Control
Network
Distillation Unit Chromalox Temperature Display (x1)
Analog Input
Trancell TI 500e weight scale (x2)
System Monitoring
MKS 750c High Pressure Absolute Pressure Transducer (x1)
hb-crio-fc
Network
Switch
Network
Pressure Control Valve (x1)
MKS GE50 Mass Flow Controller (x6)
Pressure Control
Analog Output
MKS GE50 Mass Flow Controller (x1)
Gas Flow Control
MKS 223b Differential Pressure Transducer (x1)
Gas Monitoring and Control
Magnehelic and Omega DP25 (x6)
Solenoid valve (x12)
Analog Input
Network
Gas Shed
Forward Carriage

## Slide 10: Hall B HTCC Gas Controls
Network
hb-crio-sf
Network
Switch
MKS GE250 Mass Flow Controller (x1)
Gas Flow Control
Network
Analog Input
Easidew Hygrometer (x1)
Gas Monitoring
Analog Input
MKS 223b Differential Pressure Transducer (x1)
Pressure Monitoring
Space Frame

## Slide 11: Hall B SVT Gas Controls
Network
hb-crio-sf
Network
Switch
MKS GE50 Mass Flow Controller (x1)
Gas Control
Network
Space Frame