Coil #3 Electrical Tests

Bob Forgas

08/06/03

Coil # 3 measured a dc resistance of 2.47 ohms, an inductance of 172mh, and a resistance of .16 ohms from the right coil lead to ground.  Five wires labeled #’s 28-32 go to voltage taps on the coil.  These were sequenced and look ok.

Seven wires, 24-30, in the helium tube go to seven CRT’s.  These could not be located but measured normal.

Four thermocouple wires, 31-34, in the helium tube measured normal but were not located.  The six thermocouple wires, 10-15, outside the helium tubes measured normal but could not be located.

Twelve wires, 16-27, go to six strain elements. One three wire and one two wire set go to each element.  All six elements measured normal but could not be located.