Hello,

I met with CSI to day (11/14 ) and with spoke with you on the

phone.  We need to clarify this job further before CSI can proceed.

1.  As I understand from you, the controls are for a magnet system

previously used elsewhere that you are now repackaging for use at JLAB?

Magnet History

This solenoid was built at SLAC in 1970 for the LASS spectrometer and subsequently moved to LAMPF in 1985 for inclusion in the MEGA spectrometer. The MEGA experiment has since been removed and the coils had been shipped to the Indiana University Cyclotron Facility for refurbishing and testing. The magnet support systems are now 30 years old, the instrumentation outside the coils is new which is what you see in the Hall D Solenoid Magnet diagram that I sent you.

2.  No manual exists for the previous system?

The controls are all new on the HDSSM (Hall D Solenoid Superconducting Magnet) system. No manual exists for this system.

3.  How will the signals be routed out of the cryostat.  Do you wish us to

choose the connectors and signal wiring to them from within the cryostat or

are you to specify this?  Since it appears you are building a new cryostat,

I remind you to carefully route the signals within it to prevent magnetic

flux from coupling.  This can lead to bad measurements during ramps. In any

case, we need to define the interface to the controls.

We would like to use a standard (20) pin, part no 647052, from MDC vacuum products corporation. I would appreciate your feedback on that, also if you have any other suggestions, for the wiring and design to route the signals.

4.  There are many temperature measurements.  For example, 48 Silicon

diodes.  If these are to be live in the computer at all times simultaneously

it becomes very expensive.  A single channel signal transducer costs between

$200 and $500 depending on the sensor type.  How are the various temperatures?

sensors to be handled?

We have double checked the coils and it seems that the silicon diodes have been removed.There are no SD’s in the coil or any of the other instrumentation. I will attach a new Signal list noting this change.

5.  We will need a schematic of the magnet showing the coil wiring and

Voltage tap locations.  A hand sketch would be sufficient.

Please check attachment.

6.  I understand you have 13 JT valves and 3 other types.  Each of these has a dc motor and a LVDT sensor.  Can you supply a table of these with appropriate names?

There are now 11 JT valves, 3 Electric valves (EV), and relief valves. The JT and EV valves need to be monitored.

| Name | Actuator type | Position readout | Description |
| --- | --- | --- | --- |
| 6801 JT1 | Electric Valve | LVDT | LN2 magnet bottom fill |
| 6802 JT2 | Electric Valve | LVDT | LN2 tank top fill |
| 6803 JT3 | Electric Valve | LVDT | LN2 supply Heat exchanger |
| 6804 JT4 | Electric Valve | LVDT | LHe magnet bottom Fill |
| 6805 JT5 | Electric Valve | LVDT | LHe tank top fill |
| 6806 JT6 | Electric Valve | LVDT | He supply (300K, 3 Atm) heat exchanger(Hex)(LN2) |
| 6807 JT7 | Electric Valve | LVDT | Valve after mixing He from HEx (LN2) and HEx(He) |
| 6808 JT8 | Electric Valve | LVDT | He return from LHe tank |
| 6809 JT9 | Electric Valve | LVDT | He return (4.5K, 1.2 Atm) to Hex(Helium) |
| 6810 JT10 | Electric Valve | LVDT | Left current Lead flow |
| 6811 JT11 | Electric Valve | LVDT | Right current Lead flow |
| 6812 EV | Electric Valve | 4-20 mA | Warm He return from magnet |
| 6813 EV | Electric Valve | 4-20 mA | LN2 supply from tank to magnet |
| 6814 EV | Electric Valve | 4-20 mA | LHe supply from tank to magnet |

7.  The power supply to be used is a Danfysik with identical control

interface to the Hall C dipole and Quads?  Is the dump switch built in?

The power supply is identical to the one in Hall C Dipole. Yes the dump switch is built in.

8. How many 4-channel Danfysik quench detectors does it use?

1 Danfysik detector.

Quench Detector:

| Channels | Upper/Lower/Current lead | Measurement/Taps |
| --- | --- | --- |
| CH1 | Left current lead | 1-27 |
| CH2 | Right current lead | 3-L21 bk |
| CH3 | Upper: Coil 1 Lower: Coil 4 | 3-4 29-7 |
| CH4 | Upper: Coil 2 Lower: Coil 3 | 30-5 L66-6 |

Attachments:

1. Hand sketch of the coils and their voltage taps.

2. New Signal list (Silicon diodes removed, and number of voltage taps changed).