## Slide 1: Software Specification and Software Reuse - BELLA LPA experiment
Patrick Bong
LBNL Interlock SME

## Slide 2: Introduction
The BELLA Terra-Watt interlock upgrade
  Expanded the number of lasers used in the LPA to a primary beam and a secondary beam
  Added a new laser bay
  Eliminated the relay based interlock system

## Slide 3: BELLA TW Layout

## Slide 4: Requirements Document
Requirements Document says WHAT you are going to do
  Introduction
    Project/Facility overview
    Assumptions and dependencies
  System Description
    Protective boundaries
    Protective devices
    Warning devices
    User interfaces
  System Requirements
    Protective functions
    Administrative functions
    Performance requirements
    RAMS (reliability, availability, maintainability)
Notes: This is the top level document to which all others must comply
We assume there’s going to be an accelerator, depending on funding.
The accelerator is housed in a bunker with 2 doors.
Interlock switch detects the position of the door.
Emergency off buttons 2 interior locations.
Warning sign above door with redundant lights.
Warning lights inside enclosure.
Warning annunciator inside enclosure.
Telephone at each door.
The system description does not necessarily need to describe the functionality that the requirements will provide.

## Slide 5: Software Specification
The software specification provides the details of HOW the software is going to operate.
The software specification must always conform to the details provided in the Requirements document.
The software specification may be embedded in the requirements document.

## Slide 6: Types of Specification
Verbose
  Provides a detailed explanation of the interaction between inputs and outputs.
Truth tables
  Provides the logic for a single function.
Graphical
  Uses logical symbols to describe functions.

## Slide 7: Comparison of Types
A good specification uses a combination of the specification types to provide programmer guidance and help manage the software development cycle.
  Verbose
    Very similar to the description in the requirements document.
    Must be extremely detailed to guide software development.
  Truth table
    Very detailed description of the function, but difficult to follow and understand the complete impact to the overall logic.
    Software can be derived directly from tables.
  Graphical specification
    Better representation of the overall logic.
    Logic may need to be parsed during software development.

## Slide 8: Verbose
Search and Clear
Search and clear must be started from the HMI and completed sequentially by turning the key switch at each search and clear station. When the key is turned at the first search and clear station, Access Control must be disabled preventing access to the exclusion zone while the search is in progress.
The search and clear will be limited to a 3 minute time period, after which the circuit will reset requiring the search process to be re-started from the HMI.
The search and clear process is completed by turning the High‑Energy Mode Key Selector to High-E Mode.

## Slide 9: Truth Tables

## Slide 11: Graphical Specification

## Slide 12: Code Reuse
Code reuse can be identified in the requirement or specification when identical patterns of logic appear

## Slide 13: Different Methods
Design Pattern
  A segment of code that’s copied and the variables are changed.
  Or a functional block is copied and the internal variables are modified.
Function reuse
  The block only contains logic and the variables are assigned externally.

## Slide 14: Design Pattern Reuse

## Slide 15: Functional Block
Code inside function block
Function block for reuse

## Slide 16: Conclusion
The software specification should be written so that the logic can be verified to comply with the system requirements
The language in the specification should not obfuscate the function of the logic
Code can be grouped into functional blocks and reused inside the project when recurring design patterns are recognized
New projects can use functional blocks from old project when design patterns are similar