## software
DSG Preliminary Tasks List - SoLID Solenoid I& C
Task # | Description | Able to Proceed? | Start | Finish | Assigned Person | Status | Comments
1. PLC programming based On SHMS/HMS
1.1 | Instrumentation readout (LL, PT,MFC) | Yes | 2020-04-14 |  | Pablo | In Progress | Readout for Liquid levels for N2 and He completed Readout for Pressure sensors completed
1.2 | Sensors readout (Temp, Load cells, Strain, hall sensors) | Yes | 2020-02-10 | 2020-05-15 | Pablo | Completed | Completed PLC routine to control and monitor temperature sensors in the magnet radiation screens, coil shell, neck and CCR. Completed supports readout. Need to enter look up tables
1.3 | Vacuum gauge readouts, controls and interlocks logic | Yes | 2020-04-10 | 2020-04-13 | Brian | Completed | Fault levels same as SHMS/HMS
1.4 | Heat Exchanger instrumentation control | Yes | 2020-01-15 |  | Aaron/Pablo | In Progress | Completed PLC routine to control and monitor temperature sensors on HX, Valve code added
1.5 | JT Valves- LVDT monitoring and controls |  | 2020-04-10 |  | Pablo | In Progress | Completed readout for JTV 1 to JTV7, and valve WR
1.6 | Cryo - Cooldown Operations logic |  |  |  | Pablo | In Progress
1.7 | NMR unit - PLC communication |  | 2020-04-24 |  | Brian | In Progress | Code from SHMS Q1 Hall Probe, will need to update with actual sensor calibration later
1.8 | MPS - PLC communications - ASCII (Research another reliable comm method e.g. Ethernet) |  |  |  | Brian | Completed | MPS PLC logic same as HMS PSU
1.9 | Magnetic field readout and regulation |  |  |  | Pablo | Not Started | Not required
1.1 | MPS control and monitoring - Power Up/Down |  |  |  | Brian | Completed | MPS PLC logic same as HMS PSU
1.11 | Cooldown Interlocks |  |  |  | Pablo | In progress | Looking to operation manual to verify PLC logic
1.12 | Power/MPS Interlocks - Fast/controlled ramp downs |  |  |  | Pablo | Not Started
1.13 | High speed voltage tap readout logic to archive |  | 2019-12-15 |  | Pablo | In progress | Developing PLC routine to read high speed ADC modules up to 3.3 Khz
1.14 | PLC communication test |  |  |  | Pablo | Not Started
1.15 | Sensors and Instrumentation readout/calibration test | Yes |  |  | Brian/Pablo | Not Started
1.16 | MPS-PLC Communications Test |  |  |  | Brian | Not Started
1.17 | Test, configure, tune PLC and I/O modules on Solenoid |  | 2019-12-05 |  | Pablo | In progress | Testing high speed ADC input modules. Need to be back to the lab to continue testing
2. HMI Programing
2.1 | Verify licenses access to run Factory Talk View | Yes |  |  | Pablo | Completed | Licenses available for DSG access in PHYCAD58 computer
2.2 | Configure and setup PLC - HMI communications | Yes |  |  | Pablo | Completed | Tested developed HMI screens with Cleo II PLC
2.3 | Develop custom graphics and drawings as needed | Yes |  |  | Pablo | In Progress | Completed 3D/2D models for radiation screens, coils shell, neck, cryostat, and radial and axial supports
2.4 | Develop ~ 30 screens for controls and monitoring | Yes | 2020-01-06 |  | Pablo | In Progress | Completed six screens: temperature monitor and controls (x2), axial and radial monitor, expert (x3), and CCR (x1) screens.
2.4 | Generate PLC tags list | Yes | 2020-02-04 |  | Pablo | In Progress | PLC names assigned for temperature sensors, strain, load cell, pressure, liquid levels sensors
2.5 | Create and configure Access database for archiving - OBDC mode |  | 2020-01-20 |  | Pablo | In Progress | Test version is running in DSG PLC. PLC tags to be added in FTVIEW Server PC
2.6 | Configure data base file for local data archiving |  | 2020-01-21 |  | Pablo | In Progress | Test version is running in DSG PLC
2.7 | HMI screens test |  | 2020-02-15 |  | Pablo | In Progress | Initial test for developed screens started
3. EPICS Data logging and Archiving
3.1 | Configure OPC Server - KEPServerEX |  |  |  | Pablo | Not Started
3.2 | Develop PLC IOC - OPCIocShell |  |  |  | Pablo | Not Started
3.4 | Develop data base file with PVs |  |  |  | Brian | Not Started
3.5 | Test proper data transfer between PLC tags and EPICS IOC (Read/Write) |  |  |  | Pablo | Not Started
3.6 | Setup EPICS system | Yes |  |  | Pablo | Not Started
3.7 | Configure EPICS EtherIP driver | Yes |  |  | Pablo | Not Started
3.8 | Develop CSS-BOY screens, with the same controls and monitoring features as HMI screens | Yes | 2020-04-01 |  | MaryAnn | In Progress | Completed six screens: Temperature monitor and controls (x2), axial/radial supports, expert (x3) monitoring, and CCR CSS screens. Screens under revision and testing
3.9 | Test developed CSS-BOYs off line | Yes | 2020-04-15 |  | Tyler | In Progress | Tested Temperature, axial and radial support CSS screens using Python script on CSS enviroment to create an OPI with local PVs

## hardware
DSG Preliminary Tasks List - SoLID Solenoid I& C
Category: Hardware
Task # | Description | Able to Proceed? | Start | Finish | Assigned Person | Status | Comments
1 | Arrange PLC and Instrumentation racks |  |  |  |  | In progress | Defined location of racks for 1st low current test of the magnet at the Test Lab
2 | Procure parts/components for CCS board and Motor Driver Controller Relay board | Yes | 2019-11-08 | 2020-06-10 | Marc | Completed
3 | Design of PCB for CCS boards | Yes | 2019-11-15 | 2020-02-15 | Marc | Completed | PCB design completed and sent for fabrication
4 | Solder, assembly of current source boards |  |  |  | Mindy | In Progress | One of six boards assembled
5 | Design PCB for Motor Driver Controller Relay boards | Yes | 2020-03-05 | 2020-06-10 | Marc | Completed | Original board designer company is defunct, new PCB design completed
6 | Solder, assembly of motor driver boards | Yes |  |  | Mindy | Not Started
7 | Install and assembly 24 power supplies, PLC chassis, terminal blocks, terminal strips, feedthroughs on PLC rack |  |  |  | Mindy | Not Started
8 | Install and assembly instrumentation, control devices, boards, signal conditioners, terminal strips on Instrumentation rack |  |  |  | Mindy | Not Started
9 | Wiring of instrumentation on PLC rack and Instrumentation rack as needed |  |  |  | Mindy | Not Started
10 | Installation and calibration of axial load cells on the Solenoid |  |  |  | Mindy | Not Started
11 | Wiring of sensors and instrumentation as needed from Solenoid to Instrumentation rack and PLC rack |  |  |  | Mindy | Not Started
12 | Label terminal blocks, instrumentation, wires |  |  |  | Mindy | Not Started
13 | Bench test of I&C |  |  |  | Pablo | Not Started
14 | Install and connect existing heater exchangers (HXs) |  |  |  | Mindy | Not Started

## documentation
DSG Preliminary Tasks List - SoLID Solenoid I& C
Category: Technical Documentation
Task # | Description | Able to Proceed? | Start | Finish | Assigned Person | Status | Description
1 | Generate part list status for instrumentation | Yes | 2019-11-08 |  | MaryAnn | Completed | part list completed
2 | Generate part list for CCS and Motor Controller Relay boards | Yes | 2019-11-15 |  | Marc/Peter | Completed | Part list for CSS board completed
3 | Develop P&ID / Instrumentation and Controls drawings | Yes |  |  | Mary Ann | Not Started
4 | Develop Electrical drawings | Yes |  |  | Mary Ann | In progress | 11 drawings are completed
5 | Develop PLC layout - details of I/O, Communication Mods and signals associated |  | 2020-02-25 | 2020-02-26 | Pablo | Completed | 1st version of PLC layout completed
6 | Develop Overall communication diagram |  | 2020-03-06 | 15/06/20 | Pablo /Mary Ann | Completed | 1st draft diagram completed
7 | Develop Controls and Monitoring diagram |  | 2020-12-06 | 15/06/20 | Pablo | Completed
8 | Develop Voltage Tap location diagram |  |  |  | Mary Ann | In progress | Neck 3D model developed will show voltage tap location