## All Feeders_Revised
Green | Generator Requested - Justification needed, analysis for work around vs cost of generator | generator (20kW) - for one month | B92 needs 1MW - for 1 week
Pink | Coordination Notes
Orange | Personnel (office spaces, etc) Affected
Yellow | FML to follow up on | [23 empty] | on emergency loop
[11 empty] | CC | ACC | ACC | ACC | ACC & PHY | ACC | PHY | FEL | ACC | ACC | ACC | ACC | ACC | ACC | ACC | FML | ACC | ACC | ACC | ACC | PHY | ACC | SRF
Notes | Steve Precedence | Timeframe | Week of July | Week of August | Move to 2015 if cannot accomplish in 2014 | Location | Noth LINAC Loop Primary Voltage Link (Item being workeed on - will have a shutdown) Outage denoted in days under bldg/area impacted | Also Shutdowns (to perform Primary Voltage Link work) Outage denoted in days under bldg/area impacted as "1+1" = shutdown one day prior to work being performed and shutdown one day after for final connections | Replace Secondaries | Replace Switchboards | Data Center Alt Feed | Emergency Loop | 21, E1 | 39, E2 | 49, E3 & Hall D Construction Trailer | 63, E4 & 64, Fabric Storage Bldg (power in this bldg?) | 23, ESB | FEL Trailers | 40, W4 | 45, W5 | 53A,B,C | 58 Chiller | 67, north access bldg (don’t want to go down in August (for header connections for cooling tower) - July work | 67 Power Supplies | 85 | 87 (Can’t happen until August when KTR is out of bldg) | 89 | N. LINAC East | N. LINAC Center | N. LINAC West | Hall D All Bldgs | 53, Injector | Central Chiller (basement of the test lab (one pump, one secondary pump, both primary pumps and leaves one chiller, one primary, one secondary int he basement. controls are off of the acc power, acc loop (? - could impact CUP operations) - can CUP pick up the load-might be enough. Not Automatic - system is split into two pieces. Need to check 800Ton work that is planned as they will need the central chiller to do this work.
this may have been installed during a previous job….to be checked |  | Summer 2014 | no preference from CC, but cooling does matter |  |  | northwest loop | MVSW#5 to Unitsub 5 | Unitsub 5 |  |  | 1+1 |  |  |  |  | on emergency loop SRF: 1+1
when W5 is down - sewage lift station is down (not on emergency loop) & generator will kick on for systems on the emergency loop only | 7 | Summer 2014 | 2014-08-11 |  |  | northwest loop | MVSW#2 to Unitsub W5 | Unitsub W5 | x | SWBD NA1, SWBD EM1 |  | 1+1 |  |  |  | ACC: 1+1; ACC: 1+1; ACC: 1+1
when W5 is down - sewage lift station is down (not on emergency loop) & generator will kick on for systems on the emergency loop only | 6 | Summer 2014 | 2014-08-04 |  |  | northwest loop | Unitsub W5 to Unitsub W6 | Unitsub W6 | x | SWBD NA2, MDP-INJ |  | 7 |  |  |  | ACC: 7; ACC: 7; on emergency loop ACC: no impact - emergency loop; on emergency loop ACC: 1+1
| 1 | Summer 2014 | 2014-06-30 |  |  | northwest loop | Unitsub LN1 |  | x | SWBD NL1 | [5 empty] | on emergency loop FML: 7
| 2 | Summer 2014 | 2014-07-07 |  |  | northeast loop | Unitsub LN1 to Unitsub LN2 | LN2 | x | SWBD NL2 | [5 empty] | on emergency loop FML: 7; on emergency loop ACC: 1+1; on emergency loop ACC: 7
| 3 | Summer 2014 | 2014-07-14 |  |  | northeast loop | Unitsub LN2 to Unitsub LN3 | LN3 | x | SWBD NL3 |  |  | 1+1 |  |  | on emergency loop ACC: 1+1; on emergency loop ACC: 1+1; on emergency loop ACC: 7
| 4 | Summer 2014 | 2014-07-21 |  |  | northeast loop | Unitsub LN3 |  | N/A |  |  |  | 7 |  |  | on emergency loop ACC: 7; on emergency loop ACC: 7
paul to check - Hall D recommissioning test on fridge end of June and cooldown of solenoid July 1st - might be able to fit in between these two period (if work is less than one week) | 5 | Summer 2014 | 2014-07-28 |  | x | north loop | Unitsub LN4 to MVSW#6 (manhole #8 and #9 to see what's going on - where these cables go) | 7 days to perform work, but NO outage needed | [7 empty] | on emergency loop PHY: 1+1
| 8 | Summer 2014 | 2014-08-18 |  |  | north loop | Unitsub E3 |  | x |  |  |  |  | 7 | 7 | ACC: 7; PHY: 7; FEL: 7
|  | Summer 2014 | Anytime | Anytime |  | north loop | Unitsub 5 (MH2) to NAM2 | 7 days to perform work, but NO outage needed
|  | Summer 2014 | Anytime | Anytime |  | north loop | NAM1 to MVSW#2 | 7 days to perform work, but NO outage needed
Estimated total days to perform work (55 days available) | 69
|  | 2015 |  |  |  | north loop | Unitsub W6 to 33MVA | Unitsub LN1 | [7 empty] | on emergency loop FML: 1+1; on emergency loop ACC: 7
could do this summer 2014 and can get in the manholes |  | 2015 |  |  |  | north loop | 40 MVA to MVSW #5 |  |  |  | X
|  | 2015 |  |  |  | north loop | Unitsub E3 to 40 MVA | Unitsub E3 | x | SWBD E3 |  |  |  | X | X | bar: ACC to PHY
[11 empty] | CHL | CHL | FEL | ACC | ACC | ACC | ACC | ACC | ACC | ACC | ACC | PHY
Notes | Steve Precedence | Timeframe | Week of July | Week of August | Move to 2015 if cannot accomplish in 2014 | Location | South LINAC Loop Primary Voltage Link (Item being workeed on - will have a shutdown) Outage denoted in days under bldg/area impacted | Also Shutdowns (to perform Primary Voltage Link work) Outage denoted in days under bldg/area impacted as "1+1" = shutdown one day prior to work being performed and shutdown one day after for final connections | Replace Secondaries | Replace Switchboards | 8, CHL | 8a, CHL Annex | 18, FEL | 36, GPB | 56, W3 | 68, W2 | 82, W1 | S. LINAC East | S. LINAC Center | S. LINAC West | E5 & 38, South Access Bldg | 72, Physics Storage Bldg
| 2 | Summer 2014 | 2014-07-07 |  |  | south loop | Unitsub LS1 | Unitsub LS2 | x | SWBD SL2 | CHL: 7; X ACC: 7; X ACC: 7; X ACC: 7; X ACC: 1+1; X ACC: 7
| 3 | Summer 2014 | 2014-07-14 |  |  | south loop | Unitsub LS2 | Unitsub LS3 | x | SWBD SL3 | CHL: 7; X ACC: 1+1; X ACC: 7
| 4 | Summer 2014 | 2014-07-21 |  |  | south loop | Unitsub LS3 |  | x |  | X ACC: 7
| 5 | Summer 2014 | 2014-07-28 |  |  | south loop | MVSW#7 | Unitsub GPB1 and FEL |  |  | FEL: 1+1; X ACC: 1+1
| 6 | Summer 2014 |  | 2014-08-04 |  | south loop | MVSW#3 to Unitsub FEL | Unitsub FEL |  |  | FEL: 3 or 4
|  |  | prefer to do it before the return of the dogleg magnets or after release to tunnel |  |  | south loop | Unitsub E6 |  | x |  | X ACC: 7
Estimated total days to perform work (55 days available) | 35
VESDA detection on the south loop - handles the tunnel. Can mitigate with not allowing hot work | Access control - B85, 87, 89 - if not occupied, then not a problem, but if it is occupied - then key | analog tunnel phones fed from B87 are on emergency loop - no issues
|  | 2015 |  |  |  | south loop | 40 MVA Substation to Unitsub LS4
|  | 2015 |  |  |  | south loop | MVSW#3 to 40 MVA Substation | Unitsub FEL | bar: FEL
CHL requested no K100 work during Summer 2014, requesting additional equipment - can't shutdown both CHLs at the same time (CHL1 is currently off now). K100 feed takes down CHL2 unless a temp jumper is put in. If we do it in 2015, impacts 12GeV He processing |  | 2014/2015? |  |  |  | south loop | Unitsub LS4 to Unitsub K100 | Unitsub K100 |  |  | CHL: X; X PHY: 7
CHL requested no K100 work during Summer 2014, requesting additional equipment - can't shutdown both CHLs at the same time (CHL1 is currently off now). K100 feed takes down CHL2 unless a temp jumper is put in (not until JUly could the temp line go in). If we do it in 2015, impacts 12GeV He processing |  | 2014/2015? | 2014-06-30 |  |  | south loop | Unitsub K100 | Unitsub LS1 |  | SWBD SL1 | bar: CHL; X ACC to X ACC; X ACC
CHL
Notes | Creel/Wright Precendence | Timeframe | Week of July | Week of August | Move to 2015 if cannot accomplish in 2014 | Location | CHL Loop Primary Voltage Link Outage denoted in days under bldg/area impacted | Also Shutdowns (to perform Primary Voltage Link work) Outage denoted in days under bldg/area impacted as "1+1" = shutdown one day prior to work being performed and shutdown one day after for final connections | Replace Secondaries | Replace Switchboards | CHL: 8, CHL 1 Plant
Coordinate when CHL1 (4160 - ability to restart main compressors) is down (now until early of August) | 1 | Summer 2014 | Anytime |  |  | CHL Loop | MVSW#8 to Unitsub CHL1 | Unitsub CHL1 - secondaries | x |  | CHL: 7
|  | Summer 2014 | Anytime |  |  | CHL Loop | MVSW#8 TO Unitsub CHL2 | Unitsub CHL2 - secondaries | x |  | CHL: 7
Estimated total days to perform work (55 days available) | 14
|  | 2015 |  |  |  | CHL Loop | 40 MVA Substation to MVSW#8 |  | N/A
|  | 2015 |  |  |  | CHL Loop | MVSW#8 to Unitsub CHL-AUX |  | N/A | bar: CHL
|  | 2015 |  |  |  | CHL Loop | MVSW#8 to Unitsub CHL-AUX1 |  | N/A | bar: CHL
[11 empty] | PHY | PHY | PHY | PHY | PHY & ESHQ | PHY | PHY | PHY | PHY | PHY | PHY | PHY | PHY | PHY | PHY | PHY | PHY | PHY | PHY
Notes | Walt Precedence | Timeframe | Week of July | Week of August | Move to 2015 if cannot accomplish in 2014 | Location | End Station Loop Primary Voltage Link (Item being workeed on - will have a shutdown) Outage denoted in days under bldg/area impacted | Also Shutdowns (to perform Primary Voltage Link work) Outage denoted in days under bldg/area impacted as "1+1" = shutdown one day prior to work being performed and shutdown one day after for final connections | Replace Secondaries | Replace Switchboards | Emergency Loop | 91, Beam Dump A | 92, SB1 | 94 Hall B | 94 Hall B Truck Ramp & 35 (Industrial hygiene trailer) | 95, Hall C Beam Dump | 96 Hall C | 96 Hall C Truck Ramp | 96B Hall B Gas Shed | 96C Hall C Gas Shed | 97 Counting House (system power) | 98 - Physics Chalet | 101 Hall A | 101 Hall A Truck Ramp | 101a, Hall A Gas Shed | 102 ESR 1 | 104 ESR2 | Hall A, B, C Clean Power | Counting House Utility (lights, AC)
Coutning house impact - still to meet and resolve. counting house 1st floor cooling to keep humidity down, can we use the move and cool units? - dehumidification | 9 | Summer 2014 | After July 15 |  |  | end stations | MVSW#4 to Unitsub T11, T13 | Unitsub T11, Unitsub T13, and Unitsub T4 |  | SBB3A | X ACC: 1+1; X ACC: 1+1; X ACC: 1+1 |  |  |  | 7 | 7
Coutning house impact - still to meet and resolve. counting house 1st floor cooling to keep humidity down, can we use the move and cool units? - dehumidification | 7 | Summer 2014 | beam dump |  |  | end stations | Unitsub T4 to Unitsub T3 | Unitsub T3 | x | SBB3, MDP TC | X ACC: 1+1; X ACC: 1+1; X ACC: 7; X ACC: 7; X ACC: 1+1 | [6 empty] | 7
Coutning house impact - still to meet and resolve. counting house 1st floor cooling to keep humidity down, can we use the move and cool units? - dehumidification | 4 &8 | Summer 2014 |  |  |  | end stations | Unitsub T3 to Unitsub T2 | Unitsub T2 | x | SBB3B | X ACC: 7; X ACC: 7; X ACC: 1+1; X ACC: 1+1; X ACC: 7 | [5 empty] | 1+1 | 1+1
| 4 | Summer 2014 |  |  |  | end stations | Unitsub T2 to Unitsub T1 | Unitsub T1 | x | SB ESC | X ACC: 1+1 | [5 empty] | 7 | 7
|  | Summer 2014 | After July 15 - power needed for danfysik power testing |  | x | end stations | Unitsub T1 to Unitsub T12 | Unitsub T12 |  |  | X ACC: 7
|  | Summer 2014 | potential to do first - minimal impact |  | x | end stations | Unitsub T12 to Unitsub T5 | Unitsub T5 |  | SB ESB | X ACC: 1+1
|  | Summer 2014 | beam dump, hall b ac / lcw - detectors can't lose cooling |  |  | end stations | unitsub T5 to Unitsub T6 | Unitsub T6 | x |  | CHL: 1+1; FEL: 1+1; X ACC: 7; X ACC: 1+1
|  | Summer 2014 | After July 15 |  |  | end stations | Unitsub T6 to Unitsub T8 | Unitsub T8 | x |  | CHL: 1+1; CHL: 7; FEL: 7; X ACC: 7 |  | 1+1 | 1+1 | 1+1
T7, 8, 9 close together, can we do together if we can reduce the outage (to 2 weeks) - discussions with cryo and hall A |  | Summer 2014 | After July 15 |  |  | end stations | Unitsub T8 to Unitsub T9 | Unitsub T9 | x | SB ESA | CHL: 7 | 1+1 | 7 | 7 | 7
|  | Summer 2014 | After July 15 |  |  | end stations | Unitsub T9 to Unitsub T7 | Unitsub T7 | x | SBB2A | [12 empty] | 7 |  |  | 1+1 | 1+1
|  | Summer 2014 | After July 15 |  |  | end stations | Unitsub T7 to Unitsub T10 | Unitsub T10 | x | SBB4, SBB4A | X PHY: 1+1 |  |  |  | 7 | 7
|  | Summer 2014 |  |  | x | end stations | Unitsub T10 |  |  |  | X PHY: 7
Estimated total days to perform work (55 days available) | 80
|  | 2015 |  |  |  | end stations | 40 MVA Substation to MVSW#4 | [18 empty] | X | X
ESR Cooling tower work for 2015 is a few day outage or less - just need to make the final T connection
B98 on emergency loop
VESDA in the halls and sprinkler systems down - NO HOT WORK
work going on in the halls to be defined - walt | LS systems tied to what
Fel - AC and vacuum in the beamline - drive laser AC | extension cords to generator - but not enough AC spiggots | humidity problem. Dump water skid
sprint repeaters in the tunnel are fed from inj or nL1, halls repeaters are fed from counting house

## By Impacted Area
Green | Generator Requested - Justification needed, analysis for work around vs cost of generator | generator (20kW) - for one/two month | B92 needs 1MW - for 1 week
Pink | Coordination Notes
Orange | Personnel (office spaces, etc) Affected
Yellow | FML to follow up on
[11 empty] | CC | SRF | CHL | CHL | ACC | ACC | ACC | ACC & PHY | ACC | PHY | FEL | ACC | ACC | ACC | ACC | ACC | ACC | ACC | FML | ACC | ACC | ACC | ACC | PHY | ACC | FEL | ACC | ACC | ACC | ACC | ACC | ACC | ACC | ACC | PHY | PHY | PHY | PHY | PHY | PHY & ESHQ | PHY | PHY | PHY | PHY | PHY | PHY | PHY | PHY | PHY | PHY | PHY | PHY | PHY | PHY
Notes | Order of Precedence | Timeframe | Week of July | Week of August | Move to 2015 if cannot accomplish in 2014 | Loop Location | Primary Voltage Link (Item being workeed on - will have a shutdown) Outage denoted in days under bldg/area impacted | Also Shutdowns (to perform Primary Voltage Link work) Outage denoted in days under bldg/area impacted as "1+1" = shutdown one day prior to work being performed and shutdown one day after for final connections | Replace Secondaries | Replace Switchboards | Data Center Alt Feed | Central Chiller (basement of the test lab) - can CUP pick up the load? Automatic? | 8, CHL | 8a, CHL Annex | Emergency Loop | 21, E1 | 39, E2 | 49, E3 & Hall D Construction Trailer | 63, E4 & 64, Fabric Storage Bldg (power in this bldg?) | 23, ESB | FEL Trailers | 40, W4 | 45, W5 | 53A,B,C | 58 Chiller | 67, north access bldg (don’t want to go down in August (for header connections for cooling tower) - July work | 67 Power Supplies | 85 | 87 (Can’t happen until August when KTR is out of bldg) | 89 | N. LINAC East | N. LINAC Center | N. LINAC West | Hall D All Bldgs | 53, Injector | 18, FEL | 36, GPB | 56, W3 | 68, W2 | 82, W1 | S. LINAC East | S. LINAC Center | S. LINAC West | E5 & 38, South Access Bldg | 72, Physics Storage Bldg | Emergency Loop | 91, Beam Dump A | 92, SB1 | 94 Hall B | 94 Hall B Truck Ramp & 35 (Industrial hygiene trailer) | 95, Hall C Beam Dump | 96 Hall C | 96 Hall C Truck Ramp | 96B Hall B Gas Shed | 96C Hall C Gas Shed | 97 Counting House (system power) | 98 - Physics Chalet | 101 Hall A | 101 Hall A Truck Ramp | 101a, Hall A Gas Shed | 102 ESR 1 | 104 ESR2 | Hall A, B, C Clean Power | Counting House Utility (lights, AC)
[10 empty] | Total Times Impacted | 1 | 1 | 2 | 3 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 2 | 0 | 0 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 5 | 3 | 2 | 3
[10 empty] | Total Outage (Days) | 2 | 2 | 14 | 15 | 9 | 9 | 7 | 7 | 7 | 7 | 7 | 2 | 2 | 7 | 0 | 9 | 0 | 0 | 14 | 9 | 9 | 9 | 7 | 2 | 2 | 9 | 2 | 7 | 7 | 7 | 9 | 9 | 7 | 7 | 7 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 11 | 11 | 11 | 9 | 9 | 9 | 9 | 25 | 16 | 9 | 16
|  | Summer 2014 |  |  |  | north loop | Unitsub 5 (MH2) to NAM2 | 7 days to perform work, but NO outage needed
|  | Summer 2014 |  |  |  | north loop | NAM1 to MVSW#2 | 7 days to perform work, but NO outage needed
paul to check | north - 5 | Summer 2014 |  |  |  | north loop | Unitsub LN4 to MVSW#6 (manhole #8 and #9 to see what's going on - where these cables go) | 7 days to perform work, but NO outage needed | [10 empty] | PHY: 2
this may have been installed during a previous job….to be checked |  | Summer 2014 |  |  |  | northwest loop | MVSW#5 to Unitsub 5 | Unitsub 5 |  |  | 2 | 2 |  | 1
when W5 is down - sewage lift station is down & generator will kick on for systems on the emergency loop only | north - 7 | Summer 2014 |  |  |  | northwest loop | MVSW#2 to Unitsub W5 | Unitsub W5 | x | SWBD NA1, SWBD EM1 |  |  |  |  | 2 |  |  |  | ACC: 2; ACC: 2; ACC: 2
when W5 is down - sewage lift station is down & generator will kick on for systems on the emergency loop only | north - 6 | Summer 2014 |  |  |  | northwest loop | Unitsub W5 to Unitsub W6 | Unitsub W6 | x | SWBD NA2, MDP-INJ |  |  |  |  | 7 |  |  |  | ACC: 7; ACC: 7; ACC: 2
| north - 1 | Summer 2014 |  |  |  | northwest loop | Unitsub LN1 |  | x | SWBD NL1 | [8 empty] | FML: 7
| north - 2 | Summer 2014 |  |  |  | northeast loop | Unitsub LN1 to Unitsub LN2 | LN2 | x | SWBD NL2 | [8 empty] | FML: 7; ACC: 2; ACC: 7
| north - 3 | Summer 2014 |  |  |  | northeast loop | Unitsub LN2 to Unitsub LN3 | LN3 | x | SWBD NL3 | [5 empty] | 2 |  |  | ACC: 2; ACC: 2; ACC: 7
| north - 4 | Summer 2014 |  |  |  | northeast loop | Unitsub LN3 |  | N/A | [6 empty] | 7 |  |  | ACC: 7; ACC: 7
| north - 8 | Summer 2014 |  |  |  | north loop | Unitsub E3 |  | x | [7 empty] | 7 | 7 | ACC: 7; PHY: 7; FEL: 7
| south - 2 | Summer 2014 |  |  |  | south loop | Unitsub LS1 | Unitsub LS2 | x | SWBD SL2 |  |  |  | 7 |  |  |  |  | ACC: 7; ACC: 7; ACC: 7; ACC: 2; ACC: 7
| south - 3 | Summer 2014 |  |  |  | south loop | Unitsub LS2 | Unitsub LS3 | x | SWBD SL3 |  |  |  | 7 |  |  |  |  | ACC: 2; ACC: 7
| south - 4 | Summer 2014 |  |  |  | south loop | Unitsub LS3 |  | x | [9 empty] | ACC: 7
| south - 5 | Summer 2014 |  |  |  | south loop | MVSW#7 | Unitsub GPB1 and FEL | [10 empty] | FEL: 2; ACC: 2
| south -6 | Summer 2014 |  |  |  | south loop | MVSW#3 to Unitsub FEL | Unitsub FEL | [10 empty] | FEL: 7
|  | Summer 2014 |  |  |  | south loop | Unitsub E6 |  | x | [9 empty] | ACC: 7
CHL requested no K100 work during Summer 2014 |  | 2015 |  |  |  | south loop | Unitsub LS4 to Unitsub K100 | Unitsub K100 |  |  |  |  | ? | [5 empty] | PHY: 7
CHL requested no K100 work during Summer 2014 | north - 1 | 2015 |  |  |  | south loop | Unitsub K100 | Unitsub LS1 |  | SWBD SL1 |  |  |  | ? | bar: ACC to ACC; ACC
Coordinate when CHL1 is down (now until end of August) | chl - 1 | Summer 2014 | Anytime | Anytime |  | CHL Loop | MVSW#8 to Unitsub CHL1 | Unitsub CHL1 - secondaries | x |  |  |  | 7
|  | Summer 2014 | Anytime | Anytime |  | CHL Loop | MVSW#8 TO Unitsub CHL2 | Unitsub CHL2 - secondaries | x |  |  |  | 7
| es - 9 | Summer 2014 | After July 15 |  |  | end stations | MVSW#4 to Unitsub T11, T13 | Unitsub T11, Unitsub T13, and Unitsub T4 |  | SBB3A | [43 empty] | 2 | 2 | 2 |  |  |  |  | 7 | 7
| es - 7 | Summer 2014 |  |  |  | end stations | Unitsub T4 to Unitsub T3 | Unitsub T3 | x | SBB3, MDP TC | [40 empty] | 2 |  | 2 | 7 | 7 | 2 | [7 empty] | 7
| es - 4&8 | Summer 2014 |  |  |  | end stations | Unitsub T3 to Unitsub T2 | Unitsub T2 | x | SBB3B | [40 empty] | 7 |  | 7 | 2 | 2 | 7 | [6 empty] | 2 | 2
| es - 4&8 | Summer 2014 |  |  |  | end stations | Unitsub T2 to Unitsub T1 | Unitsub T1 | x | SB ESC | [41 empty] | 2 | [10 empty] | 7 | 7
| es - 6 | Summer 2014 |  |  |  | end stations | Unitsub T1 to Unitsub T12 | Unitsub T12 | [43 empty] | 7
| es - 5 | Summer 2014 |  |  |  | end stations | Unitsub T12 to Unitsub T5 | Unitsub T5 |  | SB ESB | [8 empty] | PHY: 2
| es - 3 | Summer 2014 |  |  |  | end stations | unitsub T5 to Unitsub T6 | Unitsub T6 | x | [9 empty] | PHY: 2; PHY: 2; PHY: 7 | 2
| es - 2 | Summer 2014 | After July 15 |  |  | end stations | Unitsub T6 to Unitsub T8 | Unitsub T8 | x | [9 empty] | PHY: 2; PHY: 7; PHY: 7 | 7 | [8 empty] | 2 | 2 | 2
| es - 2 | Summer 2014 | After July 15 |  |  | end stations | Unitsub T8 to Unitsub T9 | Unitsub T9 | x | SB ESA | [8 empty] | PHY: 7 | [8 empty] | 2 | 7 | 7 | 7
| es - 1 | Summer 2014 | After July 15 |  |  | end stations | Unitsub T9 to Unitsub T7 | Unitsub T7 | x | SBB2A | [47 empty] | 7 |  |  | 2 | 2
| es - 1 | Summer 2014 | After July 15 |  |  | end stations | Unitsub T7 to Unitsub T10 | Unitsub T10 | x | SBB4, SBB4A | [46 empty] | 2 |  |  |  | 7 | 7
| es - 1 | Summer 2014 |  |  | x | end stations | Unitsub T10 | [49 empty] | 7
|  | 2015 |  |  |  | end stations | 40 MVA Substation to MVSW#4 | [53 empty] | X | X
|  | 2015 |  |  |  | CHL Loop | 40 MVA Substation to MVSW#8 |  | N/A
|  | 2015 |  |  |  | CHL Loop | MVSW#8 to Unitsub CHL-AUX |  | N/A |  |  |  | X
|  | 2015 |  |  |  | CHL Loop | MVSW#8 to Unitsub CHL-AUX1 |  | N/A |  |  |  | X
|  | 2015 |  |  |  | north loop | Unitsub W6 to 33MVA | Unitsub LN1 | [10 empty] | FML: 2; ACC: 7
|  | 2015 |  |  |  | north loop | 40 MVA to MVSW #5 |  |  |  | X
|  | 2015 |  |  |  | north loop | Unitsub E3 to 40 MVA | Unitsub E3 | x | SWBD E3 | [6 empty] | X | X | bar: ACC to PHY
|  | 2015 |  |  |  | south loop | 40 MVA Substation to Unitsub LS4
|  | 2015 |  |  |  | south loop | MVSW#3 to 40 MVA Substation | Unitsub FEL | bar: FEL
Estimated total days to perform work (55 days available) | 69 |  |  |  |  | north loop
Estimated total days to perform work (55 days available) | 35 |  |  |  |  | south loop
Estimated total days to perform work (55 days available) | 14 |  |  |  |  | CHL Loop
Estimated total days to perform work (55 days available) | 80 |  |  |  |  | end stations

## Cryo Coordination Meeting 22May
CHL | CHL1 down
CHL2 supporting both linacs at 2k
FEL is down and talked with FEL Jim Coleman. Shutting off nitrogen? Only feeds gun but gun is disassembled now - jim is checking on this
started summer maintenance and need 3 months to get work down before they can cooldown. Carbon bed is the biggest thing, and heat exchanger being worked on.
CTF | no one present at meeting
ESR | running smooth, cooldown left Q1 and this morning swapped over to cold return. Issue with cooling hall c magnet - found at it was one of the cryo pressure sensors and fixed - resumed cooldown sat night and good since.
Hall C - HMS - 4 quads and all are cold
Hall C - mid June Danfysik guy here and testing will be done end of june to mid july.
UIM | Hall A - should just turn cryo off and warm up, valve to be repaired. But need cryogens by Aug 1st
ESR#1 - power to run main compressors (2 4161), power for first 480 machine, control systems, vacuum pumps, etc.
| ESR#2 - no impact on lights and utilities for ESR#2 | ??? Walt doesn't know impacts
no outage any earlier than July 15
Cryo wants a vendor with 2 trailers of He and shutdown ESR.
He inventory still up in the air - a lot on hand and need to know what to do with this.
| If ESR stayed up until Aug 15 - then no He inventory problem or minimal problem | August 18th - dependent on CHL recovery (could be plus or minus a week) and return ESR mid Sept
| Prefer outage mid Aug/end of Aug to mitigate He inventory loss then take a full 3 week outage. | Oct 15th beam to Hall A
Hall C Magnets in september but with cool with LN2 at first
Run nitrogen during power outage
ESR#2 - put in a tie now? Creel will look at with Paul
Hall D | refrigerator is in it's shell and continue to do leak checks. Pressure test still to be done, some tubing. Then take it down to Hall D and start reinstallation. Cleanup begins with piping next week.
2 day power outage
LCLS-II | 4 major reviews coming up this FY. End of June FAC at SLAC. 3rd week in July - PDR. End of July ISR at Jlab and then a director's review immediately after
Meet again in mid June