## Slide 1: Management Safety Discussions
Welcome
Stuart Henderson
Supervisor All-Hands Meeting

## Slide 2: Agenda
‘Why’ We Are Here
SLAC Event Overview
Management Safety Discussions
Example of Management Safety Discussion
Action Plan Going Forward
Q&A

## Slide 3: ‘Why’ We Are Here
• First, thank you!
• As we continue to work, across DOE, we are seeing an increase in safety
events
• SLAC event offers us the opportunity to review how we work safely
- Parallels to our 2019 electrical event
In this meeting we want to:
  - Discuss this event: what we know, what we can learn
  - Focus on the importance of supervisors engaging with their staff members,
  - Hear from you,
  - And discuss next steps
When you come to work at Jefferson Lab, you should always remember that no work is so urgent or important that we will compromise our employees’, our Users', our subcontractors’, our visitors’ or our neighbors’ safety.

## Slide 4: We Want to Embrace Important Cultural Elements of All High-Performing Organizations

## Slide 5: Integrated Safety Management 7 Guiding Principles
ISM – 7 Guiding Principles
(1) Line Management is Responsible for the Protection of Employees, the Public and the Environment.
(2) Role and Responsibilities Are Clear. Clear and unambiguous lines of authority and responsibility for ensuring environment, safety, and health are established and maintained for all organizational levels.
(3) Competence is Commensurate with Responsibilities. Personnel possess the experience, knowledge, skills and abilities that are necessary to discharge their responsibilities.
(4) Priorities are Balanced. Resources are effectively allocated to address ES&H, programmatic and operational considerations. Protecting the employees, the public and the environment is a priority whenever activities are planned and performed.
(5) Safety Standards and Requirements are Identified. Before work is performed, the associated hazards are evaluated and an agreed- upon set of ES&H standards and requirements are established – which, when properly implemented, provide adequate assurance that employees, the public and the environment are protected from adverse consequences.
(6) Hazard Controls Are Tailored to Worked Being Performed. Administrative and engineering controls to prevent and mitigate hazards are tailored to both the work being performed and the associated hazards.
(7) Operations are Authorized. The conditions and requirements to be satisfied for operations to be initiated and conducted are clearly established and agreed upon.
We can be tempted to rush and not follow processes and procedures because we are mission focused
This can result in not only slowing down, but shutting down the mission
Hold yourself and your teammates accountable for following policies and processes
And remember the key tenets of Human Performance Improvement:
  People are fallible, even the best make errors
  Error likely situations are predictable and preventable
  Individual behavior is influenced by organizational processes, values
  People achieve high levels of performance based largely on the encouragement and reinforcement received from leaders, peers and subordinates

## Slide 6: SLAC Shock Incident on 12-27-2022
Incident Summary
By Steven Hoey

## Slide 7: SLAC Shock Incident on 12-27-2022
Summary of Preliminary Information:
Electrician in the HV Group sustained severe injuries from receiving a High Voltage shock
Electrician was part of a crew preparing multiple substations and downstream equipment for planned preventative maintenance during the holiday shutdown
He was performing a Zero Voltage Verification (ZVV) on a 12.47 kV switchgear
Crew was working under an approved Electrical Work Plan (EWP)
Crew was de-energizing and locking-out substation in accordance with the EWP which required three breakers to be opened, racked out, and LOTO lock and tag applied, and these steps were performed without incident
The energy isolation plan requires a 12kV ZVV to be performed on the switchgear
The electrician proceeded to perform the ZVV on the UPSTREAM side rather than the DOWNSTREAM side of the B626 main breaker
UPSTREAM 12kV feeder connected to the main breaker was outside the energy isolation boundary and was energized
Shock occurred

## Slide 8: SLAC Shock Incident, Continued
Work Planning
Work Plans included an EWP with HV Switching Orders (SO’s) and Lockout Tagout (LOTO) Energy Isolation Plans (EIP’s) for (1) installation of a generator to support building and equipment impacted by the outage and (2) performing LOTO and Zero Voltage Verification prior to releasing substations to contractors who would perform the PM’s
Work Plan development included; Maintenance and Ops Support Group Leader (MOS GL) walked the job to write initial plans, MOS GL walked job with the electricians, MOS GL walked job again with subcontractor after job award
MOS Support Engineer walked job to verify breakers and Switching Orders
High Voltage Supervisor reviewed the EWP, verified drawings and switching diagrams available, walked down the job and authorized the work
Workers walked the job and felt comfortable with the plan and the plan was signed off by all applicable parties, including workers, acknowledging they would adhere to steps and hazard controls
Once the EWP was fully authorized, work was scheduled

## Slide 9: SLAC Shock Incident, Continued
Day of Work
HV Crew (three electricians) attended 6:00 a.m. tailgate meeting with high voltage group personnel to discuss the EWP where workers confirmed that they understood the plan and felt comfortable with doing the work
6:30 a.m. electricians attended a broader tailgate to coordinate work for the day
Electricians started at B726 and B522 substations and visually verified breakers were racked out and applied LOTO in prep for ZVV planned for later in the day
Electricians were outfitted in NFPA Arc Flash Cat. 2 attire, (Arc rated long pants, long sleeve shirt, leather boots, hard hat and safety glasses) Cat. 2 PPE has a minimum Arc rating of 8 cal/cm2
Electricians proceeded to B626 where first ZVV was planned. Walked through a discussion of work planned including review of EWP, single line diagrams
EWP included a group LOTO on breaker 342 then a ZVV on three downstream breakers. 342 was opened, racked out and LOTO (deenergized substation B626) however the feeder to 342 from master substation 75 was energized

## Slide 10: SLAC Shock Incident, Continued
Day of Incident
Injured worker did not change into a 100cal/cm2 suit as required by SLAC Policy. He remained in his Cat. 2 (8cal/cm2) attire. He was also wearing a raincoat (Arc rated?)
Worker approached the line side of breaker 342 (energized side fed from 75), proceeded to open a cubicle door and was lifting a boot off a test point when the shock occurred
Initial Issues/Causes Identified
A 100 cal/cm2 suit was not in use, although it is required
Zero Voltage Verification was attempted on an energized breaker rather than the de-energized breakers down stream
Early fact-finding efforts incidentally discovered outdated or incorrect electrical drawings in the SLAC drawing database indicating gaps in configuration management

## Slide 11
By Johnathon Huff
Introduction to the Management Safety Discussion Tool

## Slide 12: Background: Safety Observations to Management Safety Discussions
Safety Observation (SO) Process and Data Recording Tool
  Approx. 15 years: >18,000 observations, >500 observers
  Lessons from first 15 years:
    Interaction between management and workers uniformly identified as high value support for safety culture by participants
      Discussions viewed as interrupting work
      Data recording cumbersome
      Inconsistent implementation between divisions and within divisions
  Human Performance Initiative at JLab provided an opportunity for
  rethinking and restructuring the SO process
Notes: Safety Observation (SO) Process and Data Recording Tool
  Approx. 15 years: >18,000 observations, >500 observers
  Lessons from first 15 years:
    Interaction between management and workers uniformly identified as high value support for safety culture by participants
      Ongoing work ‘interruptible for discussion’ hard to find/engage in the field; observations tended toward recording workplace conditions when discussion not ideal
      Data recording cumbersome - required data entry at observer's desk after observation was over
      Inconsistent implementation between divisions and within divisions
  Human Performance Initiative at JLab provided an opportunity for
  rethinking and restructuring the SO process

## Slide 13: Background: Opportunities for Improvement
  Analysis of 2009-19 Cause Codes for Notable Events indicated 42% of the ​
time we failed to Perform Work Within Controls – SO Process was not addressing key issues!

## Slide 14: Background, Continued
ES&H had considerable feedback on SO process and data recording tool and initiated changes
  Streamline data recording – mobile friendly
  Updated the training materials to sharpen focus on HPI
  Provided support for locating ongoing activity for engagement
  Significant support from Communications Office
    Produced training videos, re-worked/improved information content, improved website
  ES&H Manual Chapter revision underway
  End of January 2023 fanfare and rollout planned
Notes: ES&H had considerable feedback on SO process and data recording tool and initiated changes
  Partnered with IT on project to revamp SO process: streamline data recording –
  update tool, incorporate HPI, shift focus back to manager-worker interaction
  Updated the training materials to sharpen focus on HPI
  Provided supports for locating ongoing activity for engagement
  Incorporate key HPI considerations
  Conducted training and observation process using test audience (Lab Managers
  from ADs to Line Supervisors) and revised process
Pandemic conditions interrupted and subsided – Lab staff back at work
COO re-started effort end of CY 2022 to support workplace safety culture improvement
  Significant support from Communications Office
    Produced training videos, re-worked/improved information content, improved website
  ES&H Manual Chapter revision underway
  End of January 2023 fanfare and rollout planned

## Slide 15
By Bob May
Management Safety Discussions

## Slide 16: Safety Observations - History
• Lessons from first 15 years and Human Performance Initiative at JLab provided an opportunity for rethinking and restructuring the SO process
• Movement
- Away from recording found conditions
    • The Safety Warden Inspection Program is the best way to resolve workplace conditions
    • Observed conditions do not substitute for human interaction
- Toward building a culture of safety
    • Conversational interaction regarding approach to and conduct of work
    • Focus on human considerations
    • Work process design, error traps, distractions, safety consideration
Safety Observation Program
  - Started in mid 90’s as an outgrowth of
  DuPont STOP training
  - Process and recording tool design based
  on STOP pattern

## Slide 17: Management Safety Discussions (MSD)
Management Safety Discussion (MSD) Process and Data Recording Tool
  New process piloted using Test Group included line managers, ADs, non-
  manager staff
    Feedback from Test Group incorporated into new process
  New process focuses on human performance aspects of manager-worker
  interaction
  Process aimed at senior managers but available and useful for staff
  interactions
  Mobile device friendly application uses device features (voice to text) to
  facilitate data recording
  Streamlined the data collection for each interaction; data “filed in the field”
  Coupled to SO database

## Slide 18: SO / MSD Comparison Summary
Safety Observations
  Based on DuPont STOP Program
  Promoted in-the-field interaction at two principal levels
    Manager-Worker
    Worker-Worker
  Promoted cross-division observers
  Looked for unsafe conditions and unsafe behaviors
  Promoted in-the-field correction of unsafe behaviors
  Recorded and characterized both in detail in after-action report
Management Safety Discussions
  Based on long SO experience
  Places premium on “in-the-field” Manager-Worker interaction
    Same training, same principles apply for any intentional workplace discussion on safety
  Focuses on Worker activities using HPI related discussion
    Recognize error-likely situations
    Identify error avoidance methods
    Encourage and positively reinforce safe behaviors
  Simple recording using mobile device web application
  ES&H Manual and website lists details and provides examples
    Promotes cross-division partnering

## Slide 19: MSD – How Does It Work?
See https://www.jlab.org/esh/mgtsafetydis for training materials/brochures, FAQs, data entry tool
On-site
  - Solo or Team-up with partner
  Cross-divisional teams – bring “new eyes” on the work
    - Select a workplace location
    - Approach working individuals cautiously
    - Identify yourself and the purpose of your discussion
    - Dialogue - ask questions and listen
    - Reinforce the positive
  - Record
Remotely
    - Apply the same process
    - Workplace location is “Remote” - a Zoom or Teams Meeting
    - Work selection can be decided in advance

## Slide 20: A Few Dialogue Particulars
  Request information about the task such as routine maintenance, diagnostic, and emergent repair
  Get the person(s) to tell a story so that you can better understand the context of the activity
    What are the difficulties involved with this task?
    What gets in your way? What are the workarounds?
    How do you know things are going right? What are your cues that the process may be drifting?
    How do you explain what can go wrong with this task to people unfamiliar with it? What is in place to prevent this task from going wrong? If it does go wrong, how can you recover?
Be sure to compliment the person or persons on things you see going well!
Remember, you can follow-up after the discussion
  The data tool facilitates that

## Slide 21: Who Is Expected To Do This?
Focus is on providing a process to bringing upper-level managers into the workplace
Recommended frequency for different levels in a “generalized management structure” is found in the related ES&H Manual Chapter
    －Divisions/Departments have different
    missions
    －May have different priorities
      • Emphasis on certain elements depending
      on division needs
  －Room for flexibility
Anyone can MSD process
  －Can be used for a general discussion
  between two staff members
  －Feature of former SO process

## Slide 22: Recording Your Discussions
Enter who and where
  Initiator(s) only
    You can add participants and you both get credit for the discussion
  Location is keyed to site-wide database of locations
Enter when and what
  Default entry is current date and time
  Enter number of folks you talked with
Enter a brief narrative of what you talked about
  Voice to text feature of mobile device can be used to enter narrative
  Caution: it’s not always an accurate translation

## Slide 23: Recording Your Discussion, Continued
Enter Type of observation on the balance
  Strength
  Opportunity for improvement
Enter Category
  Safety, Process, Infrastructure, Other
    Describe “Other” in your narrative
Did you encounter any unsafe conditions
  If yes, you’ll be asked to describe
  Option for follow-up
You can add an attachment
  Picture from your phone
Saved attachment viewable and editable by you and other named observers
  Viewable by DSO as a default
  Reports available - generating tool

## Slide 24: Summary
Safety Observation (SO) movement to Management Safety Discussions (MSD)
  History
  Shift in focus
  Simplified process
  Simplified recording tool
Overview of available information
Discussion of MSD process
Contact: Bob May - may@jlab.org
ext. 7632
This process has been successfully piloted and is already in use.

## Slide 25
By Andrei Seryi
Leadership Experience Using MSD Tool

## Slide 26: Accelerator Division Management Safety Discussions

## Slide 27
By Stuart Henderson
Next Steps

## Slide 28: Action Plan
Conduct an Electrical Safety Committee driven “Table Top” exercise on how we do High Voltage work (scheduled next week)
Departments/Division’s will conduct rolling pauses of activities to discuss their work planning processes at the work group level and any impediments to conducting work as per procedure and examine;
  resources,
  schedule,
  off hours, emergency,
  the HPI influences etc.,
  remote workers and on-site workers,
  using the proper PPE, and,
  ensuring drawings are correct.
  The Dept/Divisions shall report out via their respective AD via the Director's Council. Complete by February 23.

## Slide 29: Action Plan, Continued
Performance Assurance will expand their ongoing assessment of oversubscription of resources as they relate to incidents across the lab.
Continue/finalize implementation of ongoing projects related to the 2019 hazardous energy events and other related process improvements at JLab;
  ePAS Phase II Rollout – beginning mid-January
  Management Safety Discussion Program - end of January rollout
      ADs will flow down expectations to their teams
  Subcontractor lifecycle process improvements – ongoing
  Deploy two modules for JLab Supervisor Fundamentals Program
  (Supervisors ES&H Training and Updated Human Performance
  Training for supervisors) FY23 3rd quarter

## Slide 30: Questions & Answers
Stuart is now taking questions
For additional questions regarding this new approach, visit the Management Safety Discussions website at
https://www.jlab.org/esh/mgtsafetydis or contact
Bob May at may@jlab.org or
Bill Rainey at wrainey@jlab.org

## Slide 31: The End
Thank you for attending.